## Slide 1
MMA3001 · Individual Project
Predicting Indoor CO2 Concentration
Using recent sensor history and building occupancy to give a 15-minute early warning for ventilation
Tanmay Gupta · Monash University · 2026
Dataset 2: Monash Smart Infrastructure · Week 5 Regression · Week 6 Integration

## Slide 2
The Problem
Why predict CO2 at all?
Most building systems only react AFTER CO2 is already too high.
What we're doing
• Predict CO2 level 15 minutes from now
• Use the last hour of sensor readings
• Include how many people are in the building
• Give ventilation a head start before air goes bad
Why it matters
• CO2 above ~800 ppm makes people less alert
• Proactive ventilation = better air + less energy
• 15 min is enough time for a building system to act
• Regression task — predicting a number, not a category
All four Week 5 regression methods were compared on real data — no single method was assumed to be best.

## Slide 3
Data — Inputs and Outputs
What goes in, what comes out
Current CO2 (ppm)
→
CO2 15 min ago
→
1-hr rolling average
→
Occupancy count (0–5)
→
Time of day & day of week
→
CO2 in 15 minutes
Source: MMA3001 Dataset 2 — Monash Smart Infrastructure. 5 occupancy zones, 5 environmental sensors.
Sensor chosen: 6012002000326
• Long continuous coverage (3+ years of real data)
• Validated against Bureau of Meteorology:
Temperature: r = +0.84 over 222 days
Humidity: r = +0.65 over 222 days
• Strong evidence it's actually measuring something real
Why the other 4 sensors were excluded
• 2 sensors: frozen internal clock — every reading has
the same timestamp → useless as time series
• 1 sensor: only 4 months of data — too short
• 1 sensor: lower quality, less validation evidence
• None of this was documented in the dataset description

## Slide 4
Methods — 4 Regression Models (Week 5)
All four compared — none assumed to be best
Each model runs through the same StandardScaler step so the comparison is fair. Same training data, same test split.
Linear Regression
Fits a straight line through the data. Simplest, most interpretable. Good baseline.
Decision Tree
Splits into if/else regions (max depth 8). Can catch combos like 'busy + afternoon' that a line misses.
SVR (RBF kernel)
Fits a smooth curve, ignores small errors. C=10, ε=0.5. Good for mild nonlinearity on a dataset this size.
Neural Network
Two hidden layers (32 + 16 units). Most flexible but also most likely to overfit on limited data.
💡 Occupancy was included as something to TEST — not assumed to be useful. Results in next slide.

## Slide 5
Results — How Each Model Performed
Chronological split: train up to 11 Mar 2026, test after
17,010 rows · 80% train / 20% test · Split by time — no random shuffling (that would inflate results)
Model
MAE (ppm)
RMSE (ppm)
R²
Linear Regression
9.012
25.579
0.358
Decision Tree
9.353
28.708
0.191
⚠ worst
SVR ← Best
8.350
25.894
0.342
✓ best
Neural Network
9.350
26.015
0.336
8.35 ppm
average error — SVR (best model)
R² ≈ 0.34
explains ~1/3 of variance — moderate result, reported honestly
Decision Tree was the worst — likely memorised the training period's patterns rather than learning something general.

## Slide 6
Key Finding — Does Occupancy Actually Help?
Tested with and without for every model
Model
R² with occupancy
R² without
Verdict
Linear Regression
0.3581
0.3579
No difference
Decision Tree
0.1914
0.3305
Gets WORSE ↓
SVR
0.3422
0.3438
No real difference
Neural Network
0.3360
0.3352
No difference
Occupancy does not improve predictions for any model. For Decision Tree it actively made things worse.
Why? The sensor has no documented room location.
• It is not in the official Sensor ID spreadsheet — no way to know which occupancy zone to pair it with.
• A separate correlation check across all 5 zones found max |r| ≤ 0.06 for CO2.
• This is a finding — it was tested properly and reported honestly, not hidden.

## Slide 7
Missing Data
What was found and how it was handled
The scale of the gaps
• Longest outage: ~636 days of missing data
• Readings are not evenly spaced
• 84,576 candidate rows in raw data
• Only 17,010 (20%) had all required values
• Rest were dropped — not filled with made-up numbers
How it was handled
• Any row missing lag / rolling average / target → dropped
• No interpolation across the 636-day gap
• Integration step needed a separate fix (next slide)
• All of this is documented in the report, not hidden
Other data quality issues found along the way:
• Two sensors had frozen internal clocks — every reading has the same timestamp. Found by profiling, not documented anywhere.
• The occupancy log file was named "MayToDec2024" but actually covers November 2023 to April 2026. Only found by checking real timestamps.

## Slide 8
Numerical Integration — Week 6
Calculating total CO2 exposure over time
A sensor gives a snapshot at each moment — but you might want to know total exposure over a day (ppm·hours = area under the curve).
🐛 Bug found during the project
• First version: resampled onto a 15-min grid, dropped missing bins, then integrated.
• Problem: readings either side of the 636-day gap looked like they were 15 minutes apart.
• Result: Simpson's gave ~1.1M ppm·h vs trapezoidal ~9.5M ppm·h. A 9× gap = something is clearly wrong.
✅ Fix: gap-aware trapezoidal rule
• Skips any panel where the two endpoints are more than 2 hours apart.
• Naive estimate: 9,543,357 ppm·h → Gap-aware: 2,305,836 ppm·h (4× difference from bridging alone)
Convergence check on a clean 41-hour gap-free window (1–3 Oct 2025):
Bin size
Trapezoidal (ppm·h)
Simpson (ppm·h)
Agreement
15 min
17,817
17,830
0.07%
30 min
18,020
18,020
0.001%
60 min
17,584
17,572
0.07%

## Slide 9
Limitations & What We'd Do Differently
Honest about what worked and what didn't
Sensor has no room location
Not in the official spreadsheet. Impossible to know which occupancy zone it belongs to — so the occupancy feature was always going to be a stretch.
R² ≈ 0.34 — only partial
The model captures about a third of what drives CO2. The rest is things we don't have data on: HVAC events, windows, doors, equipment.
Only 20% of rows usable
The 636-day gap means most of the raw data cannot form a valid training row. A richer, more continuous dataset would help.
Can't generalise to other sensors
Results apply to this one sensor in this building. Whether occupancy helps elsewhere is a different question.
If sensor room location were documented → could pick the matching zone, likely improving results.

## Slide 10
Summary
What was done, what was found
What was done
• Predicted CO2 15 min ahead using 4 regression models
• Chronological train/test split — no data leakage
• Tested occupancy feature with and without for all models
• Applied Week 6 integration to calculate CO2 exposure
• Found and fixed a real integration bug (gap bridging)
• Validated sensor against Bureau of Meteorology data
What was found
• SVR best model: 8.35 ppm average error
• R² ≈ 0.34 — moderate, reported honestly
• Occupancy does NOT improve CO2 prediction
• Sensor has no documented room — a real data gap
• CO2 driven by ventilation, not individual room counts
• 2 of 5 sensors completely unusable (frozen clock)
Best model: SVR · MAE = 8.35 ppm · R² = 0.342
github.com/tgup0010-bot/mma3001-occupancy-prediction · All numbers reproducible from scripts in reports/
Tanmay Gupta · MMA3001 · Monash University · 2026